# ERLELO v2.5

Humidity-Primary Climate Control System

Technical Documentation

Version 2.5 - November 2024

# 1. System Overview

ERLELO implements humidity-primary control using absolute humidity (AH) as the primary control variable.

## 1.1 Design Philosophy

- Dry conditions cause irreversible product damage

- Cold only slows the process (recoverable)

- Product equilibrium depends on absolute humidity

# 2. v2.5 Features

## 2.1 Dual-Layer Cascade

| Layer | Role | Deadzone | Response |
| --- | --- | --- | --- |
| Chamber (Outer) | Sets mode | 0.8 g/m³ | Slower |
| Supply (Inner) | Fast corrections | 0.5 g/m³ | Faster |

## 2.2 Humidity State Machine

| Mode | Condition | Action |
| --- | --- | --- |
| FINE | AH within deadzone | Fine temp control |
| HUMID | AH too high | Aggressive cooling |
| DRY | AH too low | Block heating |

## 2.3 Safe Initialization

On system reboot, all variables reset to defaults (0). To prevent dangerous responses to invalid data:

- 32-second initialization period after startup

- All relays held in safe OFF state during init

- Normal control logic runs (sensors, buffers, calculations)

- Relay control enabled only after initialization completes

# 3. Control Parameters (21 Total)

## 3.1 Chamber Loop (Outer)

| Parameter | Default | Div | Real | Desc |
| --- | --- | --- | --- | --- |
| deltahi_kamra_homerseklet | 15 | 10 | 1.5°C | Upper temp |
| deltalo_kamra_homerseklet | 10 | 10 | 1.0°C | Lower temp |
| temp_hysteresis_kamra | 5 | 10 | 0.5°C | Hysteresis |
| ah_deadzone_kamra | 80 | 100 | 0.8 g/m³ | AH deadzone |
| ah_hysteresis_kamra | 30 | 100 | 0.3 g/m³ | AH hyst |

## 3.2 Supply Loop (Inner)

| Parameter | Default | Div | Real | Desc |
| --- | --- | --- | --- | --- |
| deltahi_befujt_homerseklet | 10 | 10 | 1.0°C | Upper temp |
| deltalo_befujt_homerseklet | 10 | 10 | 1.0°C | Lower temp |
| temp_hysteresis_befujt | 3 | 10 | 0.3°C | Hysteresis |

## 3.3 Initialization

| Parameter | Default | Div | Real | Desc |
| --- | --- | --- | --- | --- |
| init_duration | 32 | 1 | 32s | Init period |

# 4. Initialization Behavior

When the SINUM controller reboots, all variables reset to their default values (0). This causes false emergency conditions.

## 4.1 Startup Sequence

| Time | init_complete | Relays | Activity |
| --- | --- | --- | --- |
| 0s | false | ALL OFF | Start reading sensors |
| 15s | false | ALL OFF | Buffers filling, AH calculated |
| 32s | true | NORMAL | Control enabled |

## 4.2 Why Initialization Is Needed

- Without init: Controller sees T=0°C, RH=0% and triggers emergency heating

- With init: Relays stay OFF for 32s while sensors stabilize

- Buffers fill with valid data, safe transition to normal control

# 5. Files

| File | Description |
| --- | --- |
| erlelo_kamra1.lua | Chamber controller (with init) |
| erlelo_kulso.lua | Outdoor sensor |
| erlelo_create.lua | Variable creator |
| erlelo_store.lua | ID mapper |
| erlelo_constants_editor.lua | Runtime tuning UI |
| erlelo_config_Xch.json | Config (1/2/3 chambers) |

# 6. Version History

| Version | Changes |
| --- | --- |
| v2.5 | Dual-layer cascade, directional hysteresis, state machine, all params configurable, safe initialization |
| v2.4 | Humidity-primary control, HTTP patterns fixed |
| v2.3 | Variable naming standardization |